## Slide 1: Multi-Period Optimization for Power Distribution Systems with Battery Storage
Aryan Ritwajeet Jha
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Nawaf Nazir and Mads Almassalkhi
Power System Computation Conference (2018)
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Reference [22]

## Slide 3: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Reference [22]
IEEE 123 and 13 bus systems
Unbalanced
Second Order Conic Decomposition (SOCP) used to fix State-of-Charge (SOC) for batteries at every time step.
IEEE 13 bus system
Unbalanced
STL Elements (Discrete-control)
Optimized slowly using Multi-Integer Linear Programming
Renewables + Battery
Optimized fastly using SOCP

## Slide 4: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Nawaf Nazir and Mads Almassalkhi
Power System Computation Conference (2018)
Currently at PNNL Then: PhD at University of Vermont (UVM)
Currently Assoc. Prof. at UVM

## Slide 5: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Distribution System
  Unbalanced
  Mechanical Assets?
  Significant Solar Penetration
Two Different Optimization Time-Scales
  A slow time-scale for dispatching discrete mechanical assets using Mixed-Integer Program (MIP)
  A fast time-scale for continuously monitoring DERs using SOCP.

## Slide 6: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Two Different Optimization Time-Scales
  Different Types of discrete and continuous operated devices.
    E.g. Capacitor/Reactor Banks, Line Regulators (On/Off), Load-Tap-Changing (LTC) Transformers
    Discrete states of these devices render the problem NP-hard. (So, they were NOT NP-hard anyway?)
    McCormick relaxation and linearization techniques have been used to incorporate these devices into the OPF problem for a BALANCED network. [16b]
  This necessitates the use of separate optimization loops to coordinate them.
  Mechanical assets also have operational constraints on tap changes per hour to limit wear and tear, which necessitates separation.

## Slide 7: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
Novel hierarchical OPF scheme for separation of the slow-mechanical (discrete control scheme) and fast power-electronic (continuous control scheme) on two different time-scales.
Service Transformer Layers (STL) elements dispatched optimally using Multi-Period three-phase SOCP convex relaxation techniques applied to radial distribution networks for fast corrective control.
Simultaneous charging and discharging of batteries in a convex model of 3-phase system is also analyzed and conditions are provided under which this can be avoided.

## Slide 8: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
AC Three-phase Non-Linear Model (Plant)
Minutely Dispatch of Flexible Assets (SOCP)
Hourly Dispatch of Mechanical Assets (MILP)
Forecast and Analytics
Flowchart showing the Hierarchical time-scale control algorithm

## Slide 9: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Want to minimize number of changes in mechanical discrete control components to reduce wear and tear.
  Aim: minimize from a nominal set-point using operation of these discrete assets.
  The outer loop also schedules active power exchanges of the STL elements, considering the variability of solar PV generation and forecast energy demands.
  Reactive Power Control of STL elements reserved for corrective control, in the Inner Loop.
Outer Loop Formulation: Voltage Positioning

## Slide 10: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Since discrete decision variables only take integer values, the outer loop problem becomes a mixed-integer problem, which is NP-hard.
  Branch and bound techniques can be effective on MIPs if their continuous versions are convex.
  In order to reduce the computational complexity of the outer loop, a three-phase LINEARIZED model of the network is used.
  This reduces the problem to a Mixed-Integer Linear Program (MILP).
Outer Loop Formulation : Voltage Positioning

## Slide 11: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  STL Architecture
    Four-Quadrant Control Scheme. Can supply and consume both and .
    Each STL element is composed of a renewable source of energy such as solar power and some form of storage like a battery bank.
Outer Loop Formulation : Voltage Positioning
Solar PV
Battery
Inverter
Inverter
Transmission Network.

## Slide 12: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Aim: minimize in the network.
    while keeping track of a power reference signal from the transmission level.
    while keeping the system within operational bounds.
  This program optimizes the STL elements over the fast time-scale.
  This corrective optimization loop is required to be fast ( minute).
  Three-phase SOCP used to solve the optimization problem.
    A Branch Flow Model (BFM) is used to represent the power flow equations.
Inner Loop Formulation: Corrective OPF

## Slide 13: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  The Inner Loop optimization problem can thus be formulated as:
  <INSERT formulae (26) to (36)>
    Inner Loop Objective function
    Power Balance Equation (BFM)
    Power Flow Equations (BFM)
    Line Power Flow Constraints
      Relation between BFM sub-matrices
    Voltage Constraint
    Solar PV Constraint
    Node Power Relations
    Battery State of Charge and Complementarity Constraints
Inner Loop Formulation: Corrective OPF

## Slide 14: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
Inner Loop Formulation: Corrective OPF

## Slide 15: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
Inner Loop Formulation: Corrective OPF

## Slide 16: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
    Battery State of Charge and Complementarity Constraints
    Plot of Battery Charging vs Battery Discharging without fixing an additional cost function for penalizing Simultaneous Charging Discharging (SCD).
    Additional ‘loss functions’ for 1. Penalizing SCD and 2. Respecting Battery SOC Limits.
Inner Loop Formulation: Corrective OPF

## Slide 17: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Complementarity: Charging and Discharging are complementary phenomenon for a battery, i.e. at NO time step, can a battery simultaneously undergo charging and discharging.
  Complementarity Constraints ensure that Batteries never charge and discharge simultaneously.
    But these constraints make the SOCP of the Inner Loop Non-Convex.
    One way to make it convex would be to use Mixed-Integer SOCP in the Outer Loop.
      But that would make increase the computation time substantially.
      We h0wever want solution time (to obtain a near-optimal solution) to be minute.
      So not doing that.
Relaxing Complementarity Constraint

## Slide 18: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
  Complementarity Constraints ensure that Batteries never charge and discharge simultaneously.
    But these constraints make the SOCP of the Inner Loop Non-Convex.
    One way to make it convex would be to use Mixed-Integer SOCP in the Outer Loop.
      But that would make increase the computation time substantially.
      We h0wever want solution time (to obtain a near-optimal solution) to be minute.
      Instead our approach is to relax these constraints and analyze the conditions where the optimal solution still respects them.
Relaxing Complementarity Constraint

## Slide 19: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
      Instead, their approach is to relax these constraints and analyze the conditions where the optimal solution still respects them.
      In [23b], [24b], authors provide conditions under which complementarity is satisfied in the optimal solution for an economic dispatch problem.
        In [24b], KKT conditions are analyzed for a DC model of an economic dispatch problem and they show that under realistic assumptions, complementarity is respected.
        In this paper, the analysis is extended to a distribution system setting where the objective is to minimize line losses, while considering four quadrant battery operation.
Relaxing Complementarity Constraint

## Slide 20: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
      If the objective function does NOT penalize SoC deviations from reference
Relaxing Complementarity Constraint

## Slide 21: Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices
IEEE 13
Unbalanced
has 1-phase, 2-phase, 3-phase lines
A Three-phase OLTC transformer between 633 and 634
Capacitor Banks placed at 675 and 611
STL elements added at nodes 632, 675, 680, 684
  These STL elements each have:
    Solar PV generation
    Battery capable of four-quadrant operation.
Test Cases and Numerical Simulations
Insert picture of IEEE 13 bus system.

## Slide 22: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Currently at PNNL PhD at University of Vermont (UVM)
Currently Asst. Prof. at UVM
Currently Assoc. Prof. at UVM

## Slide 23: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Distribution System
  Unbalanced
  Inverter-Interfaced
  Significant Solar Penetration
Three-Phase Unbalanced
  Non-Convex Loss-minimization problem
  Formulated as a Convex Second Order Conic Program (SOCP) for arriving at an initial solution for Non-Linear Program (NLP)
  NLP run to ensure physically realizable solution

## Slide 24: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Conditions derived to ensure that batteries do NOT simultaneously charge and discharge. (Is that a big problem?)
Tested with GridLab-D for IEEE 13 and IEEE 123.
  AC feasibility of the solutions ensured
  Near-optimal performance
  Solution time < 1 min.

## Slide 25: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
ConEd* of NY moving towards Distributed System Platforms (DSPs)
These DSPs allow for DERs to be factored into Optimization schemes for Power Generation
DERs can be Optimized to function as Virtual Batteries (VBs)
  provide energy services at different spatio-temporal scales.
* Consolidated Edison, electric utility in NY and NOT ComEd, Commonwealth Edison, electric utility in IL

## Slide 26: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Traditionally, DistFlow algorithms based on the Branch Flow Model (BFM), which are an exact non-linear formulation of the distribution power flow equations, only work on balanced single-phase equivalent networks.
  But Distribution Networks are inherently unbalanced.

## Slide 27: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  In [22] by the same authors, they have developed a three-phase convex SOCP relaxation of the multi-period OPF problem, and provided sufficient conditions which ensure the avoidance of simultaneous charging and discharging.
  In this paper, they extend the work by developing a Multi-Period SOCP-NLP algorithm that provides a near optimal and guaranteed feasible solution.

## Slide 28: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  The optimized solutions from the relaxed SOCP model, are used to initialize a Non-Linear Program (NLP) of the actual AC Power Flow, to obtain a physically realizable solution.
  Real-Power Solutions that form the energy trajectory and are obtained from the SOCP, are fixed in the NLP, leading to a decoupling of the different time-steps. (What? How?)
  As a result, the NLP solves for each time-step separately (possibly in-parallel), leading to a scalable framework. (What?)
  Validation is performed using GridLab-D.

## Slide 29: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  IEEE , Unbalanced,
  Algorithm implemented in Receding-Horizon fashion.
  Receding-Horizon means a rolling window where predictions for the next time-steps from time to are made at time and since predictions are updated at every time step, for the next time step , predictions for the next time steps from to are once again made.
  The cycle goes on.
Fig. Aggregate solar, demand and net-demand profile over a prediction horizon of

## Slide 30: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The SOCP solution outputs an optimal battery and inverter control schedule
The schedule is used by the NLP to calculate a physically realizable schedule
The physically realizable schedule is implemented by GridLab-D to determine the resulting AC Power Flows.
The forecast of demand and renewable generations are updated.
The Process

## Slide 31: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The Process
Fig. Coupling of SOCP with NLP by fixing real power solutions from SOCP and hence decoupling the NLP to obtain a feasible solution. (What? How?)
Fig. Available reactive power variation range for NLP across multiple time-steps based on the active power trajectory provided by the SOCP.

## Slide 32: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Distributed Storage and Solar PV Units randomly added to nodes
    They can supply active and reactive power through four quadrant operation.
    Each storage unit has capacity and apparent power rating
    Each solar PV unit has a rating
  Solar and Load Profile prediction horizon
    Each step

## Slide 33: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Three-phase OPF is run in a receding horizon fashion with prediction horizon of time-steps, for the dispatch of controllable assets of the network to minimize network losses.
  Set-points provided by the solutions of the SOCP are used to initialize an NLP to provide a feasible solution.
    SOCP modeled in JuMP, with Julia and solved using GUROBI.
      Multi-period SOCP has
        kvariables (k as in thousand)
        k linear constraints
        k SOC constraints

## Slide 34: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
    NLP also modeled in JuMP, but solved using IPOPT [36] using the HSL_MA86 solver [37]
      A single-period of the Multi-period SOCP has
        kvariables
        k linear constraints
        k SOC constraints
        k non-linear constraints

## Slide 35: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
    levels for both loads (low and high) and solar PV generation (low and high)
    ‘High’ implies Base Values for both Loads as well as solar PV
    ‘Low’ implies of the base values in both cases.
    Thus scenarios are modeled:
      LL (Low Solar, Low Loads)
      LH (Low Solar, High Loads)
      HL (High Solar, Low Loads)
      HH (High Solar, High Loads)
Different Solar and Load Cases

## Slide 36: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Optimality gap always below 3% for different solar penetration levels.
  Feasible solutions always ( difference).
  Solution times
  NLP total time assuming parallelized operation over every single time step.
Table: Comparison of the Optimality Gap Values of SOCP and NLP.

## Slide 37: References
[22] Nazir, N., & Almassalkhi, M. (2018). Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices. 2018 Power Systems Computation Conference (PSCC). IEEE. doi: 10.23919/PSCC.2018.8442555
[36] Wächter, A., & Biegler, L. T. (2006). On the implementation of an interior-point filter line-search algorithm for large-scale nonlinear programming. Math. Program., 106(1), 25–57. doi: 10.1007/s10107-004-0559-y
[37] HSL - Home Page. (2023, May 24). Retrieved from https://www.hsl.rl.ac.uk
[16b] Briglia, E., Alaggia, S., & Paganini, F. (2017). Distribution network management based on optimal power flow: Integration of discrete decision variables. 2017 51st Annual Conference on Information Sciences and Systems (CISS). IEEE. doi: 10.1109/CISS.2017.7926079

## Slide 38: References